## 500XL3
Zurn Wilkins Model 600XL3 |  |  | System Data (Inputs) |  |  |  | PRV Station Configuration Suggestions (Results) |  |  | 600XL3 falloff | [5 empty] | Yes (100%) | Yes | 1B | #VALUE!
|  |  | Flow Rate* | Minimum (GPM) |  | 0 | Low flow By-pass required |  | No | Flow Rate | 3/4" | 1" | 1-1/4" | 1-1/2" | 2" | Yes (partial) | No | 2B | #VALUE!
|  |  |  | Maximum (GPM) |  | 80 | Parallel PRV quantity |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | 2B-L | #VALUE!
|  |  | Pressure Reduction* | Inlet (Supply) Pressure |  | 120 | Multi-stage reduction required |  | No | 5 | 6.8 | 1 | 0.5 | 1.5 | 1.5 |  |  | 4B-L | #VALUE!
|  |  |  | Desired System (Outlet) Pressure |  | 55 | Series PRV quantity |  | 1 | 10 | 7.6 | 2 | 1 | 1.75 | 1.5
[10 empty] | 15 | 8 | 2 | 1.5 | 1.75 | 1.5
|  |  | Accessories |  |  |  | Total PRV count suggested |  | 1 | 20 | 10 | 3 | 2 | 2 | 1.5
|  |  | System pressure monitor (sensor) required? |  |  | Yes | PRV reduction ratio |  | 2.1818 | 25 | 18.1 | 5 | 2 | 2 | 1.5
[7 empty] | Suggested configuration |  | 1B | 30 | 32.7 | 7.5 | 2.5 | 2 | 2
|  |  | *Note: figure is only a representation of the system and may vary in detail between each application.* | [6 empty] | 35 |  | 14.5 | 2.5 | 3 | 2
[7 empty] | PRV Size (Inches) |  | Fall-off (PSI) @ Maximum Flow Rate | 40 |  | 25 | 4.5 | 3 | 2
600XL3 Product Specifications |  |  | #NAME? |  |  |  | 2 |  | 7.3333 | 45 |  |  | 13.8 | 4.5 | 2
Max Working Inlet Pressure (PSI) |  | 400 | [7 empty] | 50 |  |  | 20.1 | 4.5 | 2.5
Max Water Temperature (F) |  | 140 |  |  |  |  | Notes |  |  | 55 |  |  |  | 7.5 | 3
Max Reduced Pressure Setting (PSI) |  | 75 |  |  |  |  | 1)This program will specify the proper sizing and quantities of 600XL3 valves required, based on specified pressure settings & flow characteristics input into cells 'I2' through 'I5'. |  |  | 60 |  |  |  | 7.5 | 3.75
Min Reduced Pressure Setting (PSI) |  | 15 | [7 empty] | 65 |  |  |  | 10 | 4
Minimum Flow Rate (GPM) |  | 0 |  |  |  |  | 2)Max. flow rate suggested for each valve size matches typical 8ft/sec. plumbing velocity limit. |  |  | 70 |  |  |  | 13.5 | 5
[7 empty] | 3)Due to highly efficient flow performance, do not use a standard 600XL3 as a low flow bypass, only use the 600XL3DUBP w/ bypass tailpiece as low flow bypass valve options. |  |  | 75 |  |  |  | 14.5 | 5
Suggested Accessories | [9 empty] | 80 |  |  |  | 18.1 | 7.5
Gauge #: 2004-25-300 | [6 empty] | 4)Fall-off is a drop in valve outlet pressure when flowing. |  |  | 85 |  |  |  | 21 | 8
Connected Pressure Monitor: ZCSM-RP | [9 empty] | 90 |  |  |  | 23 | 8
[7 empty] | Instructions |  |  | 95 |  |  |  |  | 10
Legend | [6 empty] | 1) Enter the value for the min. & max. flow rates for the plumbing system being designed. (If the minimum flow is unknown, leave blank or enter "0"). |  |  | 100 |  |  |  |  | 11.5
Configuration. | Description | [8 empty] | 105 |  |  |  |  | 11.5
1B | One Bronze PRV | [5 empty] | 2) Enter the value for the system's inlet pressure and the desired outlet pressure. |  |  | 110 |  |  |  |  | 14.5
2B | Two Bronze PRVs | [5 empty] | 3) Select "Yes" or "No" for the pressure monitor in the Accessories section. |  |  | 115 |  |  |  |  | 15.5
[7 empty] | 4) Click the "Display Schematic Diagram" button and refer to the image below for a visual representation of the the "Suggested Configuration" for individual PRV, or PRV station. |  |  | 120 |  |  |  |  | 15.5
[10 empty] | 125 |  |  |  |  | 18.1
[10 empty] | 130 |  |  |  |  | 20
Product Data Links | [9 empty] | 135 |  |  |  |  | 20
Click for: 600XL3 Spec. Sheet |  | Click for: 600XL3(DM) (Double Male Meter) Spec. Sheet |  |  | Click for: Installation/Maint. Instructions |  |  | Click for: 3/4" Installation/Maint. Instructions |  | 140
145
150
195
200
205
210
215
220
225
230
235
240
245
250
255
260
265
270
275
280
285
290
295
300
305
310
315
[10 empty] | 320 | [5 empty] | 4" 8ft/sec = 318 GPM
325
330
335
340
345
350
355
360
365
370
375
380
385
390
395
400
405
410
415
420
425
430
435
440
445
450
455
460
465
470
475
480
485
490
495
500