## SBF-Typ._Install_P-Schedule
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Inlet Pressure (PSI)
SOV-1 | Wilkins Model 850XL | Shall be full port, all-brass or bronze construction with replaceable Teflon seat ring, two-piece union or three-piece bolted design as scheduled herein. | Body: Low lead Bronze ASTM B 584 Ball: Chrome plated low lead brass Seat: TFE virgin teflon | 2-1/2" - 10" | 175 PSI | 135
Shut-off Valve Schedule
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Inlet Pressure (PSI) | Rated Flow (GPM) | Installation |  |  | Accessories / Trim
WS-1 | Wilkins SXL | The “Y” type strainer shall be a manufactured import certified to NSF/ANSI/CAN 61. The main body and cover shall be low lead cast bronze (ASTM B 806), the strainer screen shall be 20 mesh 300 series stainless steel and accessible for maintenance without removing the device from the line. The “Y” type strainer shall be a ZURN WILKINS Model SXL. | Main valve body: Cast Bronze ASTM B 806 Access cover & plug: Cast Bronze ASTM B 806 Screens: 20 Mesh Stainless Steel, 300 Series O-ring: Buna Nitrile | 3/8" - 3" | 300 psi @ 180°F WOG | 135 | 0-500 | Install wye pattern strainers for water on supply side of each [control valve] [water pressure-reducing valve] [solenoid valve] [and] [pump]. Local codes shall govern installation requirements. Unless otherwise specified, the assembly shall be mounted in accordance with the latest edition of the Uniform Plumbing Code. If installed below grade, be certain adequate drainage is provided to prevent the device from being submerged. Horizontal installation with the strainer cap facing downward is the preferred installation orientation; however the strainer will provide protection in any orientation. |  |  | Blow Down Valve: Wilkins Model 850XL (Ballv Valve)
Strainer Schedule
Location / Tag | Make / Model | Specification Description | Material | Size (in) | MWWP (PSI) | Inlet Pressure (PSI) | Pressure Loss (PSI) | Outlet Pressure (PSI) | Rated Flow (GPM) | Installation | Accessories / Trim
BFP-1 | Wilkins' 975XL3 | Wilkins' Model 975XL3 ASSE® 1013 Listed Reduced Pressure Principle Backflow Preventer (certified to NSF/ANSI/CAN 61) is rated for 180°F, 175 PSI, comes standard with low lead bronze (ASTM B 584) full port ball valves, main body and access covers. The seat ring and all internal polymers shall be Noryl™. The seat disc elastomers shall be silicone. Test cocks shall be accessible from the top of the assembly. | Main valve body: Low Lead Cast Bronze ASTM B 584 Access covers: Low Lead Cast Bronze ASTM B 584 Fasteners: Stainless Steel, 300 Series Elastomers: Silicone (FDA Approved) Buna Nitrile (FDA Approved) Polymers: Noryl™ Springs: Stainless Steel, 300 Series Ball valve handles: Stainless Steel | 1/2" - 2" | 300 psi @ 180°F WOG | 135 | < 15 | 120 | 8 - 160 | Installation of Backflow Preventers must be performed by qualified, licensed personnel. The installer should be sure the proper device has been selected for the particular installation. Faulty installation could result in an improperly functioning device. Comply with authorities having jurisdiction. | Wye Strainer: SXL Air Gap: AG-4, AG-5, AG-8 Test Kit: TG-3, TG-5
Backflow Prevention Assembly Schedule
Location / Tag | Make / Model | Specification Description | Material | Size (in) | Inlet Pressure (PSI) | Outlet Pipe Size (Type) | Installation
AG-X | Wilkins AG-8 | Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection. | Body: Cast grey iron, epoxy painted Bolts: Steel, zinc plated | 1/2" - 1" | N/A | 1" NPT | Local codes shall govern installation requirements. To be installed in accordance with the manufacturers' instructions and the latest edition of the Uniform Plumbing Code.
AG-Y | Wilkins AG-4 | Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection. | Body: Cast grey iron, epoxy painted Bolts: Steel, zinc plated | 1-1/4"-1-1/2" | N/A | 1" NPT | Local codes shall govern installation requirements. To be installed in accordance with the manufacturers' instructions and the latest edition of the Uniform Plumbing Code.
AGZ | Wilkins AG-5 | Air-Gap Fitting: ASME A112.1.2, matching backflow-preventer connection. | Body: Cast grey iron, epoxy painted Bolts: Steel, zinc plated | 2" | N/A | 2" NPT | Local codes shall govern installation requirements. To be installed in accordance with the manufacturers' instructions and the latest edition of the Uniform Plumbing Code.
Air Gap Schedule