## FIXTURE
PLUMBING FIXTURE SCHEDULE (V1 - October 2025) |  |  | Express Spec Hub: Supporting Spec Sheet Packages & Product Guide
[10 empty] | WSFU |  |  | MINIMUM PIPE CONNECTION SIZES
TAG | FIXTURE | MANUFACTURER | MODEL NUMBER | DESCRIPTION | ACTUATION | INSTALLATION | FIXTURE MATERIAL/ FINISH | FLOW | DFU | CW | HW | Power | DRAIN | VENT | COLD | HOT | NOTES & ACCESSORIES
WC-1 | Water Closet | Zurn Zurn | Z.WC.S.HYD Z1201/Z1202 | Z.WC.S.HYD system with Z5615-BWL wall hung water closet, 1.28 GPF battery operated ZER6000AV-HET-HYD battery operated hydro-power gear driven, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with a clog resistant, filter bypass and Z5955SS-EL elongated, open front white toilet seat with stainless steel check hinges. Z5610-NUT-EXT-KIT - Retrofit nut kit for extending carrier studs from existing wall. Z5977-NEO - NeoSeal gasket kit for wall mounted bowls Provide with Zurn Z1201 or Z1202 floor affixed wall mounted water closet carrier (rated to min. 500 lbs. static load). | Sustainable Sensor | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Battery | 4" | 2" | 1" | -
WC-2 | Water Closet, ADA (17" Install) | Zurn Zurn | Z.WC.S.HYD Z1201/Z1202 | Z.WC.S.HYD system with Z5615-BWL wall hung water closet, 1.28 GPF battery operated ZER6000AV-HET-HYD battery operated hydro-power gear driven, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with a clog resistant, filter bypass and Z5955SS-EL elongated, open front white toilet seat with stainless steel check hinges. Z5610-NUT-EXT-KIT - Retrofit nut kit for extending carrier studs from existing wall. Z5977-NEO - NeoSeal gasket kit for wall mounted bowls Provide with Zurn Z1201 or Z1202 floor affixed wall mounted water closet carrier (rated to min. 500 lbs. static load). Mount to ADA height, per state code, latest edition. (17") | Sustainable Sensor | Wall Mount ADA | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Battery | 4" | 2" | 1" | -
WC-3 | Water Closet, Floor Mount | Zurn | Z.WC4.S.HYD | Z.WC4.S.HYD system with Z5655-BWL1 floor mount water closet, 1.28 GPF battery operated ZER6000AV-HET-HYD battery operated hydro-power gear driven, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with a clog resistant, filter bypass and Z5955SS-EL elongated, open front white toilet seat with stainless steel check hinges. Z5972-COMB - Closet bolt/wax ring kit. | Sustainable Sensor | Floor Mount | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Battery | 4" | 2" | 1" | -
WC-4 | Water Closet, Floor Mount, ADA | Zurn | Z.WC4.AS.HYD | Z.WC4.S.HYD system with Z5665-BWL1 floor mount water closet, 1.28 GPF battery operated ZER6000AV-HET-HYD battery operated hydro-power gear driven, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with clog resistant, filter bypass and Z5955SS-EL elongated, open front white toilet seat with stainless steel check hinges. Z5972-COMB - Closet bolt/wax ring kit. | Sustainable Sensor | Floor Mount ADA | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Battery | 4" | 2" | 1" | -
WC-5 | Water Closet | Zurn Zurn | Z.WC1.S Z1201/Z1202 | Z.WC1.S system with Z5615-BWL wall hung water closet, 1.1 GPF battery operated ZER6000AV-ONE-SM battery operated exposed, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with clog resistant, filter bypass and Z5955SS-EL elongated, open front white toilet seat with stainless steel check hinges. Z5610-NUT-EXT-KIT - Retrofit nut kit for extending carrier studs from existing wall. Z5977-NEO - NeoSeal gasket kit for wall mounted bowls Provide with Zurn Z1201 or Z1202 floor affixed wall mounted water closet carrier (rated to min. 500 lbs. static load). | Sensor | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Valve | 1.1 GPF | 3 | 10 |  | Battery | 4" | 2" | 1" | -
WC-6 | Water Closet, ADA (17" Install) | Zurn Zurn | Z.WC1.S Z1201/Z1202 | Z.WC1.S system with Z5615-BWL wall hung water closet, 1.1 GPF battery operated ZER6000AV-ONE-SM battery operated exposed, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with clog resistant, filter bypass and Z5955SS-EL elongated, open front white toilet seat with stainless steel check hinges. Z5610-NUT-EXT-KIT - Retrofit nut kit for extending carrier studs from existing wall. Z5977-NEO - NeoSeal gasket kit for wall mounted bowls Provide with Zurn Z1201 or Z1202 floor affixed wall mounted water closet carrier (rated to min. 500 lbs. static load). Mount to ADA height, per state code, latest edition. (17") | Sensor | Wall Mount ADA | Vitreous China Fixture Chrome-Plated Brass Valve | 1.1 GPF | 3 | 10 |  | Battery | 4" | 2" | 1" | -
WC-7 | Water Closet | Zurn | Z.WC4.S | Z.WC4.S system with Z5655-BWL1 floor mount water closet, 1.28 GPF battery operated ZER6000AV-HET-SM battery operated exposed, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with clog resistant, filter bypass and Z5955SS-EL elongated, open front white toilet seat with stainless steel check hinges. Z5972-COMB - Closet bolt/wax ring kit. | Sensor | Floor Mount | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Battery | 4" | 2" | 1" | -
WC-8 | Water Closet, ADA | Zurn | Z.WC4.AS | Z.WC4.S system with Z5665-BWL1 floor mount water closet, 1.28 GPF battery operated ZER6000AV-HET-SM battery operated exposed, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with clog resistant, filter bypass and Z5955SS-EL elongated, open front white toilet seat with stainless steel check hinges. Z5972-COMB - Closet bolt/wax ring kit. | Sensor | Floor Mount ADA | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Battery | 4" | 2" | 1" | -
WC-9 | Water Closet | Zurn Zurn | Z.WC2.M Z1201/ Z1202 | Z.WC2.M Complete high efficiency 1.28 GPF manual actuated wall mounted commercial water closet system with Z6000AV-HET exposed, manually activated chrome-plated closet diaphragm flushometer for either left or right hand supply, Z5955SS-EL open front commercial toilet seat, Z5615-BWL wall mounted vitreous china water closet. Z5610-NUT-EXT-KIT - Retrofit nut kit for extending carrier studs from existing wall. Z5977-NEO - NeoSeal gasket kit for wall mounted bowls. Provide with Zurn Z1201 or Z1202 floor affixed wall mounted water closet carrier (rated to min. 500 lbs. static load). | Manual | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Manual | 4" | 2" | 1" | -
WC-10 | Water Closet, ADA (17" Install) | Zurn Zurn | Z.WC2.M Z1201/ Z1202 | Z.WC2.M Complete high efficiency 1.28 GPF manual actuated wall mounted commercial water closet system with Z6000AV-HET exposed, manually activated chrome-plated closet diaphragm flushometer for either left or right hand supply, Z5955SS-EL open front commercial toilet seat, Z5615-BWL wall mounted vitreous china water closet. Z5610-NUT-EXT-KIT - Retrofit nut kit for extending carrier studs from existing wall. Z5977-NEO - NeoSeal gasket kit for wall mounted bowls Provide with Zurn Z1201 or Z1202 floor affixed wall mounted water closet carrier (rated to min. 500 lbs. static load). Mount to ADA height, per state code, latest edition. (17"). | Manual | Wall Mount ADA | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Manual | 4" | 2" | 1" | -
WC-11 | Water Closet | Zurn | Z.WC4.M | Z.WC4.M Complete high efficiency 1.28 GPF manual actuated floor mounted commercial water closet system with Z6000AV-HET exposed, manually activated chrome-plated closet flushometer for either left or right hand supply, Z5955SS-EL open front commercial toilet seat and Z5655-BWL1 floor mounted vitreous china water closet. Z5972-COMB - Closet bolt/wax ring kit. | Manual | Floor Mount | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Manual | 4" | 2" | 1" | -
WC-12 | Water Closet ADA | Zurn | Z.WC4.AM | Z.WC4.AM Complete high efficiency 1.28 GPF manual actuated floor mounted commercial water closet system with Z6000AV-HET exposed, manually activated chrome-plated closet flushometer for either left or right hand supply, Z5955SS-EL open front commercial toilet seat and Z5665-BWL1 floor mounted vitreous china water closet. Z5972-COMB - Closet bolt/wax ring kit. | Manual | Floor Mount ADA | Vitreous China Fixture Chrome-Plated Brass Valve | 1.28 GPF | 3 | 10 |  | Manual | 4" | 2" | 1" | -
UR-1 | Urinal | Zurn Zurn | Z.UR1.S.HYD Z1222 | Z.UR1.S.HYD battery sensor, Z5755-U urinal with reduced splash back, strainer and ZER6003AV-ULF-HYD battery operated hydro-power gear driven, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with a clog resistant, filtered bypass. 0.125 GPF Z1222 Carbon steel, type II wall urinal support. | Sustainable Sensor | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Valve | 0.125 GPF | 2 | 5 |  | Battery | 2" | 2" | 3/4" | -
UR-2 | Urinal, ADA | Zurn Zurn | Z.UR1.S.HYD Z1222 | Z.UR1.S.HYD battery sensor, Z5755-U urinal with reduced splash back, strainer and ZER6003AV-ULF-HYD battery operated hydro-power gear driven, sensor flush valve with manual override, TPE, chloramine resistant, dual seat diaphragm with a clog resistant, filtered bypass. 0.125 GPF Z1222 Carbon steel, type II wall urinal support. Install per ADA guidelines. | Sustainable Sensor | Wall Mount ADA | Vitreous China Fixture Chrome-Plated Brass Valve | 0.125 GPF | 2 | 5 |  | Battery | 2" | 2" | 3/4" | -
UR-3 | Urinal | Zurn Zurn | Z.UR1.S.TM Z1222 | Z.UR1.S.TM battery sensor, Z5755-U urinal with reduced splash back, strainer and ZER6003AV-ULF-TM flush valve with the dual action of the ceramic disc cartridge and motor gear-driven operation and manual override button. 0.125 GPF Z1222 Carbon steel, type II wall urinal support system with adjustable bearing plate | Sensor | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Valve | 0.125 GPF | 2 | 5 |  | Battery | 2" | 2" | 3/4" | -
UR-4 | Urinal, ADA | Zurn Zurn | Z.UR1.S.TM Z1222 | Z.UR1.S.TM battery sensor, Z5755-U urinal with reduced splash back, strainer and ZER6003AV-ULF-TM flush valve with the dual action of the ceramic disc cartridge and motor gear-driven operation and manual override button. 0.125 GPF Z1222 Carbon steel, type II wall urinal support system with adjustable bearing plate | Sensor | Wall Mount ADA | Vitreous China Fixture Chrome-Plated Brass Valve | 0.125 GPF | 2 | 5 |  | Battery | 2" | 2" | 3/4" | -
UR-5 | Urinal | Zurn Zurn | Z.UR1.M Z1222 | Z.UR1.M Complete high efficiency 0.125 GPF manual actuated, wall mounted commercial urinal system with Z5755-U Omni-Flo top spud urinal, Z6003AV-ULF exposed, manually activated chrome-plated urinal flushometer for either left or right hand supply 0.125 GPF Z1222 Carbon steel, type II wall urinal support system with adjustable bearing plate | Manual | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Valve | 0.125 GPF | 2 | 5 |  | Manual | 2" | 2" | 3/4" | -
UR-6 | Urinal, ADA (17" Install) | Zurn Zurn | Z.UR1.M Z1222 | Z.UR1.M Complete high efficiency 0.125 GPF manual actuated, wall mounted commercial urinal system with Z5755-U Omni-Flo top spud urinal, Z6003AV-ULF exposed, manually activated chrome-plated urinal flushometer for either left or right hand supply. 0.125 GPF Z1222 Carbon steel, type II wall urinal support system with adjustable bearing plate | Manual | Wall Mount ADA | Vitreous China Fixture Chrome-Plated Brass Valve | 0.125 GPF | 2 | 5 |  | Manual | 2" | 2" | 3/4" | -
LAV-1 | Lavatory, Double | Zurn Zurn | Z5004.02.01.5RC.TMV-1 Z1240-EZR | Z5004.02.01.5RC.TMV-1 Sundara Surf double white basin, solid surface (acrylic resin & aluminum trihydrate); Z6953XL-TMV-1 faucet with spray outlet; and Z6953-SD soap dispenser to right of faucet. 0.5 GPM Z1240-EZR Carbon steel type II lavatory support system for Sundara with adjustable uprights and header plates. | Sustainable Sensor | Wall Mount | Solid Surface (Acrylic Resin & Aluminum Trihydrate) Chrome Plated Faucet | 0.5 GPM | 2 | 2 | 2 | Battery | 2X 1-1/2" | 1-1/2" | 2X 1/2" | 2X 1/2"
LAV-2 | Lavatory | Zurn Zurn | Z.L7.S.HYD Z1231EZ-WL | Z.L7.S.HYD complete sensor hand washing system with Z5344 20" x 18" vitreous china wall hung lavatory, ZG6955, ADA compliant, battery powered, chrome plated gooseneck sensor faucet with thermostatic mixing valve, Z8743-PC chrome plated cast brass solid top grid strainer, Z8700-8B-PC P-trap and Z8804-XL-LR-LK-PC series supply stop kit. 0.5 GPM Z1231EZ-WL Universal Type II Lavatory carrier with waste line sleeve | Sustainable Sensor | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Faucet | 0.5 GPM | 1 | 1 | 1 | Battery | 1-1/4" | 1-1/4" | 1/2" | 1/2"
LAV-3 | Lavatory, ADA | Zurn Zurn | Z.L7.S.HYDA Z1231EZ-WL | Z.L7.S.HYDA complete sensor hand washing system with Z5344 20" x 18" vitreous china wall hung lavatory; ZG6955-TMV-1 ADA compliant, battery powered, chrome plated sensor faucet with point of use thermostatic mixing valve and vandal-resistant, non-aerated outlet; Z8746-PC chrome plated cast brass open grid strainer; Z8700-8B-PC series P-trap and Z8804-XL-LR-LK-PC supply stop kit; Z8946-3-NT combination trap, supply, and drain protector. 0.5 GPM Z1231EZ-WL Universal Type II Lavatory carrier with waste line sleeve | Sustainable Sensor | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Faucet | 0.5 GPM | 1 | 1 | 1 | Battery | 1-1/4" | 1-1/4" | 1/2" | 1/2"
LAV-4 | Lavatory | Zurn Zurn | Z.L6.S Z1231EZ-WL | Z.L6.S Complete sensor hand washing system includes Z5344 20”x18” vitreous china wall hung lavatory with ZG6915-XL-TMV-1, ADA compliant, hydropowered, chrome plated 4” wide base sensor faucet with thermostatic mixing valve, Z8743-PC chrome plated cast brass solid top grid strainer, Z8700-8B-PC P-trap, and Z8804-XL-LR-LK-PC supply stop kit. 0.5 GPM Z1231EZ-WL Universal Type II Lavatory carrier with waste line sleeve | Sensor | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Faucet | 0.5 GPM | 1 | 1 | 1 | Battery | 1-1/4" | 1-1/4" | 1/2" | 1/2"
LAV-5 | Lavatory, ADA | Zurn Zurn | Z.L6.SA Z1231EZ-WL | Z.L6.SA Complete sensor hand washing system includes Z5344 20”x18” vitreous china wall hung lavatory with ZG6915-XL-TMV-1, ADA compliant, hydropowered, chrome plated 4” wide base sensor faucet with point of use thermostatic mixing valve and vandal resistant; non-aerated outlet; Z8746-PC chrome plated cast brass open grid strainer and offset tailpiece; Z8700-8B-PC P-trap; Z8804-XL-LK-PC supply stop kit Z8946-3-NT combination trap, supply and drain protector. 0.5 GPM Z1231EZ-WL Universal Type II Lavatory carrier with waste line sleeve | Sensor | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Faucet | 0.5 GPM | 1 | 1 | 1 | Battery | 1-1/4" | 1-1/4" | 1/2" | 1/2"
LAV-6 | Lavatory | Zurn Zurn | Z.L3.M Z1231EZ-WL | Z.L3.M Complete manual hand washing system includes Z5344 20”x18” vitreous china wall hung lavatory with Z81104-XL-3M polished chrome plated cast brass faucet with a 0.5 gym aerator, Z8743-PC chrome plated cast brass solid top grid strainer, Z8700-8B-PC P-trap, and Z8804-XL-LR-LK-PC supply stop kit. 0.5 GPM Z1231EZ-WL Universal Type II Lavatory carrier with waste line sleeve | Manual | Wall Mount | Vitreous China Fixture Chrome-Plated Brass Faucet | 0.5 GPM | 1 | 1 | 1 | Manual | 1-1/4" | 1-1/4" | 1/2" | 1/2"
SH-1 | Shower Valve, Tub & Shower | Zurn | Z7301-SSC-MT | Z7301-SSC-MT Single handle pressure balancing mixing tub and shower unit, ceramic control cartridge with stainless steel balancing piston, built in reverse connection capability, two service stops / check stops, and adjustable limit stop. All exposed trim and handle are metal with polished nickel chrome plated surface. Supplied with the -S1 2.0 GPM shower head, ABS aerator, arm and flange in chrome plated finish. Four port pressure balancing mixing valve with a tub port included with 1/2" female copper sweat connections. | Manual | Wall Mount | Polished Nickel Chrome Plated | 2.0 GPM | 2 | 2 | 2 | Manual | - | - | 1/2" | 1/2"
SH-2 | Shower Valve, Tub & Shower | Zurn | Z7302-SS-MT-DV2P-HW-H9-S9 | Z7302-SS-MT-DV2P-HW-H9-S9 Single handle pressure balancing mixing tub and shower unit, ceramic control cartridge with stainless steel balancing piston, built in reverse connection capability, two service stops / check stops, and adjustable limit stop. All exposed trim and handle are metal with polished nickel, chrome plated surface. Supplied with a two-way brass diverter valve, 60" flexible metal hose, 24" mounting bar, supply elbow and flange, -H9 1.6 GPM hand held shower head, -S9 1.5 GPM static shower head, arm, flange, and (T2) diverter tub spout with chrome plated finish. Four port pressure balancing mixing valve with a tub port plug included with 1/2" NPT female thread connections. | Manual | Wall Mount | Polished Nickel Chrome Plated | 1.6 GPM | 2 | 2 | 2 | Manual | - | - | 1/2" | 1/2"
MB-1 | Mop Basin | Zurn | Z1996-24-AW-BS-HH-MH-SDL-SF-WG | Z1996-24-AW-BS-HH-MH-SDL-SF-WG Mop Service Basin 24 x 24 x 10 [610 x 610 x 254] Molded high density composite basin in white. Complete with Stainless Steel Bumper Guard, Hose and Hose Bracket, Mop Hanger, Stainless steel dome strainer with lint basket and locking nut, service faucet 2.2 GPM, and type 304 stainless steel wall guard | Manual | Floor Mount | High Density Composite Fixture Chrome Plated Brass | FLOW: 2.2 GPM; DFU: 2; WSFU CW: 3; WSFU HW: 3; WSFU Power: Manual
EWC-1 | Bottle Filler Water Cooler (ADA), Bi-Level, Filtered, Refrigerated | Elkay | LZSTL8WSBPRO | LZSTL8WSBPRO Elkay Pro Filtration® Bottle Filling Station & Bi-Level ADA Cooler Refrigerated Ultra-Capacity Lead Reduction. Chilling Capacity of 8.0 GPH of 50°F drinking water. Features shall include Antimicrobial*, Automatic Filter Status Reset, Energy Savings, Filtered, Green Ticker™, Hands Free, Laminar Flow, Real Drain, Visual Filter Monitor, Alcove Light, Pro Filtration System, Top Mount Quick Filter Change, Stainless Steel Alcove, Automatic Filter Flush. Furnished with Flexi-Guard ® Safety Bubbler. Electronic Bottle Filler Sensor with Electronic Front and Side Bubbler Pushbar activation. Product shall be Wall Mount (On Wall), for Indoor applications, serving 2 station(s). Unit shall be certified to UL 399 and CAN/CSA C22.2 No. 120. Included filter FL10 - Elkay Pro Filtration® Ultra-Capacity Lead + Microplastics 10000 gal. filter | Sensor Bottle Filler Pushbar Bubbler | Wall Mount | Black Stainless Stainless Steel Alcove | FLOW: 8 GPH; DFU: 0.5; WSFU CW: 0.5; WSFU Power: Hard-Wired | FL10 - Elkay Pro Filtration® Ultra-Capacity Lead + Microplastics 10000 gal. Filter
EWC-2 | Bottle Filler Water Cooler (ADA), Single, Filtered, Refrigerated | Elkay | LZS8WSBPRO | LZS8WSBPRO Elkay Pro Filtration® Bottle Filling Station & Single ADA Cooler Refrigerated Ultra-Capacity Lead Reduction. Chilling Capacity of 8.0 GPH of 50°F drinking water. Features shall include Antimicrobial*, Automatic Filter Status Reset, Energy Savings, Filtered, Green Ticker™, Hands Free, Laminar Flow, Real Drain, Visual Filter Monitor, Alcove Light, Automatic Filter Flush, Stainless Steel Alcove, Pro Filtration System, Top Mount Quick Filter Change. Furnished with Flexi-Guard ® Safety Bubbler. Electronic Bottle Filler Sensor with Electronic Front and Side Bubbler Pushbar activation. Product shall be Wall Mount (On Wall), for Indoor applications, serving 1 station(s). Unit shall be certified to UL 399 and CAN/CSA C22.2 No. 120. Included filter FL10 - Elkay Pro Filtration® Ultra-Capacity Lead + Microplastics 10000 gal. filter | Sensor Bottle Filler Pushbar Bubbler | Wall Mount | Black Stainless Stainless Steel Alcove | FLOW: 8 GPH; DFU: 0.5; WSFU CW: 0.5; WSFU Power: Hard-Wired | FL10 - Elkay Pro Filtration® Ultra-Capacity Lead + Microplastics 10000 gal. Filter
EWC-3 | Bottle Filler Water Cooler (ADA), Bi-Level, In-Wall, Filtered, Refrigerated | Elkay | LZWS-LRPBM28K | LZWS-LRPBM28K ezH2O® Bottle Filling Station with Bi-Level Integral SwirlFlo® Fountain Filtered Refrigerated Stainless. Chilling Capacity of 8.0 GPH of 50°F drinking water. Features shall include Antimicrobial*, Filtered, Green Ticker™, Hands Free, Laminar Flow, Real Drain, Visual Filter Monitor. Furnished with Flexi-Guard ® Safety Bubbler. Electronic Bottle Filler Sensor with Mechanical Front Bubbler Button activation. Product shall be Wall Mount (Inwall Frame/Plate), for Indoor applications, serving 2 station(s). Unit shall be certified to UL 399 and CAN/CSA C22.2 No. 120. Included filter 51300C - WaterSentry® Lead + Microplastics NSF/ANSI Certified 3000 Gal 12 Month Filter. Mounting frame included | Sensor Bottle Filler Pushbar Bubbler | In-Wall | Stainless Steel | FLOW: 8 GPH; DFU: 0.5; WSFU CW: 0.5; WSFU Power: Hard-Wired | 51300C - WaterSentry® Lead + Microplastics NSF/ANSI Certified 3000 Gal 12 Month Filter
EWC-4 | Bottle Filler Water Cooler (ADA), Single, In-Wall, Filtered, Refrigerated | Elkay | LZWS-LRPBM8K | LZWS-LRPBM8K ezH2O® Bottle Filling Station with Integral SwirlFlo® Fountain Refrigerated Filtered Refrigerated Stainless. Chilling Capacity of 8.0 GPH of 50°F drinking water. Features shall include Antimicrobial*, Filtered, Green Ticker™, Hands Free, Laminar Flow, Real Drain, Visual Filter Monitor. Furnished with Flexi-Guard ® Safety Bubbler. Electronic Bottle Filler Sensor with Mechanical Front Bubbler Button activation. Product shall be Wall Mount (Inwall Frame/Plate), for Indoor applications, serving 1 station(s). Unit shall be certified to UL 399 and CAN/CSA C22.2 No. 120. Included filter 51300C - WaterSentry® Lead + Microplastics NSF/ANSI Certified 3000 Gal 12 Month Filter. Mounting frame included | Sensor Bottle Filler Pushbar Bubbler | In-Wall | Stainless Steel | FLOW: 8 GPH; DFU: 0.5; WSFU CW: 0.5; WSFU Power: Hard-Wired | 51300C - WaterSentry® Lead + Microplastics NSF/ANSI Certified 3000 Gal 12 Month Filter
EWC-5 | Bottle Filler Water Cooler (ADA), Bi-Level, Filtered, Refrigerated, Vandal Resistant | Elkay | LVRCTL8WSK | LVRCTL8WSK Elkay ezH2O® Vandal-Resistant Bottle Filling Station & Bi-Level Cooler Filtered Refrigerated Stainless. Chilling Capacity of 8.0 GPH of 50°F drinking water. Features shall include Filtered, Green Ticker™, Laminar Flow, Real Drain, Vandal Resistant, Visual Filter Monitor. Furnished with Vandal Resistant bubbler. Electronic Bottle Filler Button with Mechanical Front Bubbler Button activation. Product shall be Wall Mount (On Wall), for Indoor + Outdoor applications, serving 2 station(s). Unit shall be certified to UL 399 and CAN/CSA C22.2 No. 120. Included filter 51300C - WaterSentry® Lead + Microplastics NSF/ANSI Certified 3000 Gal 12 Month Filter. | Manual Bottle Filler Pushbar Bubbler | Wall Mount | Stainless Steel | FLOW: 8 GPH; DFU: 0.5; WSFU CW: 0.5; WSFU Power: Hard-Wired | 51300C - WaterSentry® Lead + Microplastics NSF/ANSI Certified 3000 Gal 12 Month Filter
EWC-6 | Bottle Filler Water Cooler (ADA), Single, Filtered, Refrigerated, Vandal Resistant | Elkay | LVRC8WSK | LVRC8WSK ezH2O® Vandal-Resistant Bottle Filling Station & Single Cooler Filtered Refrigerated Stainless. Chilling Capacity of 8.0 GPH of 50°F drinking water. Features shall include Filtered, Green Ticker™, Laminar Flow, Real Drain, Vandal Resistant, Visual Filter Monitor. Furnished with Vandal Resistant bubbler. Electronic Bottle Filler Button with Mechanical Front Bubbler Button activation. Product shall be Wall Mount (On Wall), for Indoor + Outdoor applications, serving 1 station(s). Unit shall be certified to UL 399 and CAN/CSA C22.2 No. 120. Included filter 51300C - WaterSentry® Lead + Microplastics NSF/ANSI Certified 3000 Gal 12 Month Filter. | Manual Bottle Filler Pushbar Bubbler | Wall Mount | Stainless Steel | FLOW: 8 GPH; DFU: 0.5; WSFU CW: 0.5; WSFU Power: Hard-Wired | 51300C - WaterSentry® Lead + Microplastics NSF/ANSI Certified 3000 Gal 12 Month Filter
NOTES: FIXTURES TO BE MOUNTED IN ACCORDANCE WITH LOCAL PLUMBING CODES AND ADA REQUIREMENTS
Tag = Mark
Note on F5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Add power per Daniel Blatto