SECTION 21 10 00 – WATER BASED FIRE-SUPPRESSION SYSTEMS

ZURN WILKINS GUIDE SPECIFICATION

The following specification text has been prepared by Zurn Wilkins assist design professionals in the preparation of a specification for water based fire protection system pressure reducing valves.

Utilize these paragraphs to insert text into Specification Section 21 10 00 – Water Based Fire-Suppression Systems or similarly titled section governing this work.

The following should be noted in using this document:

Optional text requiring a selection by the user is enclosed within brackets and as [Red.] text.

Items requiring user input are enclosed within brackets and as red text, e.g.: "[2] [__] years."

For assistance on the use of the products in this section, contact Zurn Elkay by calling 1-855-663-9876 or visit their website www.zurn.com

PART 1 – GENERAL

- SUBMITTALS

Action Submittals:

Product Data: Manufacturer’s product data sheets with descriptive, product attributes, including optional variations required, and indications of certifications/listings.

Informational Submittals

Operation and maintenance manual data.

- part 2 - products

- MANUFACTURERS

- Contract Documents are based on Zurn Wilkins. www.zurn.com

- Substitutions: [Refer to Division 01.] [Not permitted.]

- FIRE PROTECTION Pressure Reducing Valve

- Zurn Wilkins Model ZW209FPHP FM approved and cULus listed diaphragm actuated and pilot controlled pressure reducing valve sized as shown and complete with:

- an ASTM A 536 ductile iron main valve cover, and a globe style main body with an inlet and outlet to suit the connecting piping

- a fusion epoxy coating on all ferrous metal surfaces

- a stainless steel disc guide and seat

- a guided stainless steel valve stem

- a Nylon reinforced Buna-N diaphragm

- a 2-way normally open, direct acting, adjustable, spring loaded, diaphragm actuated pressure reducing pilot assembly with “wye” type strainer, inlet and outlet pressure gauges with 3-way gauge isolation valve, copper tubing and brass fittings, and pilot control field adjustable from 30 psi to 300 psi

- [Optional items as follows:

      - [“C” Model 40XL2 hydraulic check]

      - [“Z” ZPI position Indicator]

      - [“Z2” ZPI2 stainless steel dry position indicator]

      - [“SP” all stainless steel pilot system fittings, valve and tubing]

      - [“RV” pilot on reverse side]

- part 3 - EXECUTION

- INSTALLATION OF FIRE PROTECTION Pressure Reducing Valve

- Provide a pressure reducing valve assembly in wet pipe fire suppression piping where shown.

- Install the valve in accordance with applicable NFPA 13/14 requirements. Ensure that a properly sized (minimum ½”) relief valve is installed on the downstream side of the pressure control valve.

- Adjust the valve to the required downstream pressure and inspect and test the valve in accordance with requirements of NFPA 25.

- END OF SECTION