- Section 224000 
Plumbing Fixtures

  - PART 1  GENERAL

    - SECTION INCLUDES

      - Flush valve water closets.

      - Tank type water closets.

      - Dual flush water closets.

      - Bidets.

      - Waterless urinals.

      - Wall hung urinals.

      - Lavatories.

      - Wall-hung, solid surface, multistation lavatory units.

      - Glass-fiber-reinforced concrete, multistation lavatory units.

      - Wall-hung, multistation wash fountains.

      - All-in-one lavatory system.

      - All-in-one sanitary cabinet.

      - Combination faucet and hand dryer.

      - Deck-mounted hand dryers.

      - Sinks.

      - Under-lavatory pipe supply covers.

      - Bathtubs and showers.

      - Institutional ligature-resistant showers.

      - Walk-in soaking tubs.

      - Shower receptors.

      - Showers.

      - Outdoor showers.

      - Indoor drinking fountains.

      - Outdoor drinking fountains.

      - Bottle filling drinking fountains.

      - Bottle filling stations (fountain retrofit kit).

      - Electric water coolers.

      - Bi-level, electric water coolers.

      - Wash fountains.

      - Mop sinks.

      - Service sinks.

      - Vacuum waste-collection systems.

      - Emergency eye and face wash.

      - Emergency showers.

      - Whirlpool baths.

    - RELATED REQUIREMENTS

      - Section 011000 - Summary:  Owner-furnished fixtures.

      - Section 064100 - Architectural Wood Casework:  Counters for sinks and lavatories.

      - Section 079200 - Joint Sealants:  Sealing joints between fixtures and walls and floors.

      - Section 114000 - Foodservice Equipment:  Food service sinks.

      - Section 115300 - Laboratory Equipment:  Laboratory sinks.

      - Section 123600 - Countertops:  Counters for sinks and lavatories.

      - Section 221005 - Plumbing Piping.

      - Section 221006 - Plumbing Piping Specialties.

      - Section 223000 - Plumbing Equipment.

      - Section 260583 - Wiring Connections:  Electrical characteristics and wiring connections.

    - REFERENCE STANDARDS

      - ADA Standards - 2010 ADA Standards for Accessible Design; 2010.

      - ASHRAE Std 18 - Methods of Testing for Rating Drinking-Water Coolers with Self-Contained Mechanical Refrigeration; 2008 (Reaffirmed 2013).

      - ASME A112.6.1M - Floor-Affixed Supports for Off-the-Floor Plumbing Fixtures for Public Use; 1997 (Reaffirmed 2017).

      - ASME A112.18.1 - Plumbing Supply Fittings; 2024.

      - ASME A112.18.9 - Protectors/Insulators for Exposed Waste and Supplies on Accessible Fixtures; 2011 (Reaffirmed 2022).

      - ASME A112.19.1 - Enamelled Cast Iron and Enamelled Steel Plumbing Fixtures; 2024.

      - ASME A112.19.2 - Ceramic Plumbing Fixtures; 2024.

      - ASME A112.19.3 - Stainless Steel Plumbing Fixtures; 2022.

      - ASME A112.19.4M - Porcelain Enameled Formed Steel Plumbing Fixtures; 1994 (Reaffirmed 2009).

      - ASME A112.19.5 - Flush Valves and Spuds for Water Closets, Urinals, and Tanks; 2022.

      - ASME A112.19.14 - Six-Liter Water Closets Equipped with a Dual Flushing Device; 2013 (Reaffirmed 2018).

      - ASME A112.19.15 - Bathtubs/Whirlpool Bathtubs with Pressure Sealed Doors; 2012 (Reaffirmed 2022).

      - ASSE 1014 - Performance Requirements for Backflow Prevention Devices for Hand-Held Showers; 2020.

      - ASSE 1016 - Performance Requirements for Automatic Compensating Valves for Individual Showers and Tub/Shower Combinations; 2017 (Reaffirmed 2021).

      - ASSE 1070 - Performance Requirements for Water Temperature Limiting Devices; 2020.

      - ASTM C177 - Standard Test Method for Steady-State Heat Flux Measurements and Thermal Transmission Properties by Means of the Guarded-Hot-Plate Apparatus; 2019, with Editorial Revision (2023).

      - ASTM C518 - Standard Test Method for Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus; 2021.

      - ASTM C1822 - Standard Specification for Insulating Covers on Accessible Lavatory Piping; 2021.

      - ASTM D570 - Standard Test Method for Water Absorption of Plastics; 2022.

      - ASTM D638 - Standard Test Method for Tensile Properties of Plastics; 2022.

      - ASTM D696 - Standard Test Method for Coefficient of Linear Thermal Expansion of Plastics Between -30°C and 30°C with a Vitreous Silica Dilatometer; 2016.

      - ASTM D785 - Standard Test Method for Rockwell Hardness of Plastics and Electrical Insulating Materials; 2023.

      - ASTM E84 - Standard Test Method for Surface Burning Characteristics of Building Materials; 2023d.

      - ASTM G21 - Standard Practice for Determining Resistance of Synthetic Polymeric Materials to Fungi; 2015, with Editorial Revision (2021).

      - CSA B45.8/IAPMO Z403 - Terrazzo, Concrete, Composite Stone, and Natural Stone Plumbing Fixtures; 2018.

      - FM (AG) - FM Approval Guide; Current Edition.

      - IAPMO PS 106 - Tileable Shower Receptors and Shower Kits; 2015, with Editorial Revision.

      - IAPMO Z124 - Plastic Plumbing Fixtures; 2022, with Editorial Revision.

      - IAPMO Z1700/CSA B45.13 - Vacuum Waste-Collection Systems; 2019.

      - ICC A117.1 - Accessible and Usable Buildings and Facilities; 2017.

      - ISFA 2-01 - Classification and Standards for Solid Surfacing Material; 2013.

      - ITS (DIR) - Directory of Listed Products; Current Edition.

      - NEMA LD 3 - High-Pressure Decorative Laminates; 2005.

      - NSF 61 - Drinking Water System Components - Health Effects; 2024.

      - NSF 372 - Drinking Water System Components - Lead Content; 2024.

      - UL (DIR) - Online Certifications Directory; Current Edition.

    - SUBMITTALS

      - See Section 013000 - Administrative Requirements for submittal procedures.

      - Product Data:  Provide catalog illustrations of fixtures, sizes, rough-in dimensions, utility sizes, trim, and finishes.

      - Samples:  Submit two lavatory supply fittings.

      - Manufacturer's Instructions:  Indicate installation methods and procedures.

      - Sustainable Design Documentation:  Submit appropriate evidence that materials used in potable water systems comply with the specified requirements.

      - Maintenance Data:  Include fixture trim exploded view and replacement parts lists.

      - Waterless Urinals:  Submit recommended frequency of maintenance and parts replacement, methods of cleaning, sources of replacement supplies and parts.

      - Warranty:  Submit manufacturer warranty and ensure forms have been completed in Owner's name and registered with manufacturer.

      - Maintenance Materials:  Furnish the following for Owner's use in maintenance of project.

        - See Section 016000 - Product Requirements for additional provisions.

        - Extra Faucet Washers:  One set of each type and size.

        - Extra Lavatory Supply Fittings:  One set of each type and size.

        - Extra Shower Heads:  One of each type and size.

        - Extra Toilet Seats:  One of each type and size.

        - Flush Valve Service Kits:  One for each type and size.

        - Extra Waterless Urinal Trap Seals and Supplies:  One year's worth, based on normal, expected use of facility of this type.

    - QUALITY ASSURANCE

      - Manufacturer Qualifications:  Company specializing in manufacturing the type of products specified in this section, with minimum three years of documented experience.

    - MOCK-UP

      - Provide mock-up of typical bathroom group.

      - Mock-up may remain as part of the Work.

    - DELIVERY, STORAGE, AND HANDLING

      - Accept fixtures on-site in factory packaging. Inspect for damage.

      - Protect installed fixtures from damage by securing areas and by leaving factory packaging in place to protect fixtures and prevent use.

    - WARRANTY

      - See Section 017800 - Closeout Submittals for additional warranty requirements.

      - Provide five year manufacturer warranty for electric water cooler.

  - PART 2  PRODUCTS

    - GENERAL REQUIREMENTS

      - Potable Water Systems:  Provide plumbing fittings and faucets that comply with NSF 61 and NSF 372 for maximum lead content; label pipe and fittings.

      - Water Efficiency:  EPA WaterSense label is required for all water closets, urinals, lavatory faucets, and showerheads.

      - Maximum Fixture or Faucet Supply Pressure:  60 psi (4.1 bar) unless stated otherwise.

    - REGULATORY REQUIREMENTS

      - Comply with applicable codes for installation of plumbing systems.

      - Comply with UL (DIR) requirements.

      - Perform work in accordance with local health department regulations.

      - Provide certificate of compliance from Authority Having Jurisdiction indicating approval of installation.

    - FLUSH VALVE WATER CLOSETS

      - Water Closets:

        - Vitreous china, ASME A112.19.2, floor mounted, siphon jet flush action, china bolt caps.

        - Bowl:  ASME A112.19.2; 16.5 inches (420 mm) high with elongated rim.

        - Flush Valve:  Exposed (top spud).

        - Flush Operation:  Sensor operated.

        - Handle Height:  44 inches (1117 mm) or less.

        - Inlet Size:  1-1/2 inches (38 mm).

        - Trapway Outlet:  4 inch (100 mm, DN).

        - Color:  White.

        - Manufacturers:

          - Zurn Industries, LLC; ______:  www.zurn.com/#sle.

      - Flush Valves:

        - Valve Supply Size:  1 inch (25 mm, DN).

        - Valve Outlet Size:  1-1/2 inches (40 mm, DN).

        - Manufacturers:

          - Zurn Industries, LLC; ZEMS Series:  www.zurn.com/#sle.

      - Toilet Seats:

        - Manufacturers:

          - Zurn Industries, LLC; ______:  www.zurn.com/#sle.

        - Plastic:  Black finish, open front, extended back, self-sustaining hinge, brass bolts, with cover.

      - Water Closet Carriers:

        - Manufacturers:

          - Zurn Industries, LLC; Z1201-N:  www.zurn.com/#sle.

        - ASME A112.6.1M; adjustable cast iron frame, integral drain hub and vent, adjustable spud, lugs for floor and wall attachment, threaded fixture studs with nuts and washers.

    - TANK TYPE WATER CLOSETS

      - Manufacturers:

        - Zurn Industries, LLC; ______:  www.zurn.com/#sle.

      - Wall-Hung Bowl:

        - ASME A112.19.2; vitreous china, reverse trap, whirlpool action close-coupled closet combination with regular rim, insulated vitreous china closet tank with fittings and lever flushing valve, chrome plated bolt caps.

        - Water Consumption:  1.6 gal (6 L) per flush, maximum.

        - Handle Height:  44 inches (1117 mm) or less.

        - Trapway Outlet:  4 inch (100 mm, DN).

        - Water Closet Carrier:

          - Manufacturers:

            - Zurn Industries, LLC; ______:  www.zurn.com/#sle.

          - ASME A112.6.1M; adjustable cast iron frame, integral drain hub and vent, adjustable spud, lugs for floor and wall attachment, threaded fixture studs with nuts and washers.

    - DUAL FLUSH WATER CLOSETS

      - Manufacturers:

        - Zurn Industries, LLC; ________:  www.zurn.com/#sle.

      - ASME A112.19.14; high efficiency and low consumption, vitreous china, dual flush, tank type.

        - Bowl:  Elongated.

        - Rough In:  12 inch (305 mm).

        - Seat:  Manufacturer’s standard or recommended elongated closed front seat with lid.

        - Color:  White.

    - WATERLESS URINALS

      - Manufacturers:

        - Zurn Industries, LLC; ______:  www.zurn.com/#sle.

      - Wall-hung, vitreous china, complying with ASME A112.19.2; one piece bowl and shields, with integral trap, back outlet, carrier, and necessary fittings.

        - Trapway Outlet Assembly:  Siphon trap type not requiring additional water for drainage of urine; liquid trap seal that is lower specific gravity than water or urine and is biodegradable; completely enclosed cartridge intended to be replaced periodically or refillable liquid trap seal; tamperproof but removable for cleaning and replacement.

        - Projection From Wall:  Approximately 14 inches (360 mm).

        - Width:  Approximately 19 inches (490 mm).

        - Color:  White.

    - WALL HUNG URINALS

      - Manufacturers:

        - Zurn Industries, LLC; _____:  www.zurn.com/#sle.

      - Vitreous china, ASME A112.19.2, wall hung with side shields and concealed carrier.

        - Consumption Volume:  1.0 gal (3.7 L) per flush, maximum.

        - Flush Valve:  Exposed (top spud).

        - Flush Operation:  Sensor operated.

        - Trapway Outlet:  Integral.

      - Flush Valves:

        - Manufacturers:

          - Zurn Industries, LLC; ZEMS Series:  www.zurn.com/#sle.

      - Urinal Carriers:

        - Manufacturers:

          - Zurn Industries, LLC; Z1221:  www.zurn.com/#sle.

        - ASME A112.6.1M; cast iron and steel frame with tubular legs, lugs for floor and wall attachment, threaded fixture studs for fixture hanger, bearing studs.

    - STALL URINALS

      - ASME A112.19.2; vitreous china slope front stall urinal with integral flushing rim, removable stainless steel strainer 3/4 inch (19 mm) top spud.

      - Trapway Outlet:  Integral.

      - Flush Valves:

        - Manufacturers:

          - Zurn Industries, LLC; ______:  www.zurn.com/#sle.

      - Stall Urinal Carriers:

        - Manufacturers:

          - Zurn Industries, LLC; ______:  www.zurn.com/#sle.

        - ASME A112.6.1M; cast iron and steel frame with tubular legs, lugs for floor and wall attachment, threaded fixture studs for fixture hanger, bearing studs.

    - LAVATORIES

      - Manufacturers:

        - Zurn Industries, LLC; ______:  www.zurn.com/#sle.

      - Wall-Hung Basin:

        - Porcelain-Enamelled Cast Iron:  ASME A112.19.1; white, rectangular basin with splash lip, front overflow, soap depression, and hanger. Size as indicated on drawings with 4-inch (100 mm) centerset spacing.

        - Carrier:

          - ASME A112.6.1M; cast iron and steel frame with tubular legs, lugs for floor and wall attachment, threaded studs for fixture hanger, bearing plate and studs.

          - Manufacturers:

            - Zurn Industries, LLC; Z1231:  www.zurn.com/#sle.

      - Supply Faucet:

        - Deck Mounted Faucet Manufacturers:

          - Zurn Industries, LLC; Aqua Sense Series:  www.zurn.com/#sle.

        - ASME A112.18.1; chrome plated combination supply fitting with pop-up waste, water economy aerator with maximum flow of 2.2 gpm (8.3 L/min), indexed handles.

      - Metered Faucet:

    - WALL-HUNG, SOLID SURFACE, MULTISTATION LAVATORY UNITS

      - Manufacturers:

        - Zurn Industries, LLC; Sundara Drift Handwashing System:  www.zurn.com/#sle.

      - Description:  Rectilinear, level-surface deck, seamless and integral elongated basin, with stainless steel enclosed pedestal cabinet.

      - Deck and Bowl Material:  Fabricate from molded engineered stone material consisting of natural quartz, granite, and other minerals in a matrix of thermoset acrylic modified bio-based polyester resin and meeting requirements of IAPMO Z124.

      - Surface Burning Characteristics:  Smoke developed index less than 450, and flame spread index less than 25, Class A, when tested in accordance with ASTM E84.

      - Number of Wash Stations:  Two.

      - Unit Length:  _____ inches (_____ mm).

      - Soap Dispenser:

      - Color:  As selected by Architect from manufacturer's full line.

      - Faucet Drilling:  4 inch (100 mm) centerset drilling.

      - Access Panel:  Stainless steel.

      - Support Frame:  Wall-mounted, heavy gauge, stainless steel.

    - MOP SINKS

      - Manufacturers:

        - Zurn Industries, LLC; ______:  www.zurn.com/#sle.

  - PART 3  EXECUTION

    - EXAMINATION

      - Verify that walls and floor finishes are prepared and ready for installation of fixtures.

      - Verify that electric power is available and of the correct characteristics.

      - Confirm that millwork is constructed with adequate provision for the installation of counter top lavatories and sinks.

    - PREPARATION

      - Rough-in fixture piping connections in accordance with minimum sizes indicated in fixture rough-in schedule for particular fixtures.

    - INSTALLATION

      - Install each fixture with trap, easily removable for servicing and cleaning.

      - Provide chrome-plated rigid or flexible supplies to fixtures with loose key stops, reducers, and escutcheons.

      - Install components level and plumb.

      - Install and secure fixtures in place with wall supports and bolts.

      - Solidly attach water closets to floor with lag screws. Lead flashing is not intended to hold fixture in place.

    - INTERFACE WITH WORK OF OTHER SECTIONS

      - Review millwork shop drawings. Confirm location and size of fixtures and openings before rough-in and installation.

    - ADJUSTING

      - Adjust stops or valves for intended water flow rate to fixtures without splashing, noise, or overflow.

    - CLEANING

      - Clean plumbing fixtures and equipment.

      - See Section 017419 - Construction Waste Management and Disposal for additional requirements.

    - PROTECTION

      - Protect installed products from damage due to subsequent construction operations.

      - Do not permit use of fixtures by construction personnel.

      - Repair or replace damaged products before Date of Substantial Completion.

    - SCHEDULES

      - Fixture Heights:  Install fixtures to heights above finished floor as indicated.

        - Water Closet:

          - Standard:  15 inches (380 mm) to top of bowl rim.

          - Accessible:  18 inches (455 mm) to top of seat.

        - Water Closet Flush Valves:

          - Standard:  11 inches (280 mm) min. above bowl rim.

          - Recessed:  10 inches (255 mm) min. above bowl rim.

        - Urinal:

          - Standard:  22 inches (560 mm) to top of bowl rim.

          - Accessible:  17 inches (430 mm) to top of bowl rim.

        - Lavatory:

          - Standard:  31 inches (785 mm) to top of basin rim.

          - Accessible:  34 inches (865 mm) to top of basin rim.

        - Drinking Fountain:

          - Child:  30 inches (760 mm) to top of basin rim.

          - Standard Adult:  40 inches (1015 mm) to top of basin rim.

          - Accessible:  36 inches (915 mm) to top of spout.

        - Shower Heads:

          - Adult Male:  69.5 inches (1765 mm) to bottom of head.

          - Adult Female:  64.5 inches (1640 mm) to bottom of head.

          - Child:  58.5 inches (1490 mm) to bottom of head.

      - Fixture Rough-In

        - Water Closet (Flush Valve Type):

          - Cold Water:  1 Inch (25 mm).

          - Waste:  4 Inch (100 mm).

          - Vent:  2 Inch (50 mm).

        - Water Closet (Tank Type):

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  4 Inch (100 mm).

          - Vent:  2 Inch (50 mm).

        - Bidet:

          - Hot Water:  1/2 Inch (15 mm).

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  1-1/2 Inch (40 mm).

          - Vent:  1-1/4 Inch (32 mm).

        - Urinal, Waterless:

          - Waste:  2 Inch (50 mm).

          - Vent:  1-1/2 Inch (40 mm).

        - Urinal (Flush Valve Type):

          - Cold Water:  3/4 Inch (20 mm).

          - Waste:  2 Inch (50 mm).

          - Vent:  1-1/2 Inch (40 mm).

        - Urinal (Tank Type):

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  2 Inch (50 mm).

          - Vent:  1-1/2 Inch (40 mm).

        - Lavatory:

          - Hot Water:  1/2 Inch (15 mm).

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  1-1/2 Inch (40 mm).

          - Vent:  1-1/4 Inch (32 mm).

        - Sink:

          - Hot Water:  1/2 Inch (15 mm).

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  1-1/2 Inch (40 mm).

          - Vent:  1-1/4 Inch (32 mm).

        - Service Sink:

          - Hot Water:  1/2 Inch (15 mm).

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  2 Inch (50 mm).

          - Vent:  1-1/2 Inch (40 mm).

        - Service Sink:

          - Hot Water:  1/2 Inch (15 mm).

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  3 Inch (80 mm).

          - Vent:  1-1/2 Inch (40 mm).

        - Drinking Fountain:

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  1-1/4 Inch (32 mm).

          - Vent:  1-1/4 Inch (32 mm).

        - Bathtub:

          - Hot Water:  1/2 Inch (15 mm).

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  1-1/2 Inch (40 mm).

          - Vent:  1-1/4 Inch (32 mm).

        - Shower:

          - Hot Water:  1/2 Inch (15 mm).

          - Cold Water:  1/2 Inch (15 mm).

          - Waste:  1-1/2 Inch (40 mm).

          - Vent:  1-1/4 Inch (32 mm).

- END OF SECTION