- Section 400506 
Couplings, Adapters, and Specials for Process Piping

  - PART 1  GENERAL

    - SECTION INCLUDES

      - Check valves.

      - Backflow preventers.

      - Pressure reducing valves.

      - Pressure relief valves.

      - Air release devices.

      - Vacuum breakers.

      - Sample ports.

      - Strainers.

      - Flanges, unions, and couplings.

      - Valved drains.

      - Piping and equipment insulation.

      - Electrical heat tracing tape.

    - RELATED REQUIREMENTS

      - Section 134713 - Cathodic Protection:  Cathodic protection for buried steel, ductile iron, gray iron, and stainless steel components.

      - Section 400552 - Process Valves:  Valves for process control.

      - Section 402340 - Sanitary Wastewater Process Piping:  Requirements for connections to piping.

      - Section 460106 - Operation and Maintenance Manual:  Operating and Maintenance Data.

      - Section 460500 - Common Work Results For Water and Wastewater Equipment:  Requirements applicable to all equipment.

    - REFERENCE STANDARDS

      - ASME B1.20.1 - Pipe Threads, General Purpose, Inch; 2013 (Reaffirmed 2018).

      - ASME B1.20.2M - Pipe Threads, 60 Deg, General Purpose; 2006 (Reaffirmed 2011).

      - ASME B16.1 - Gray Iron Pipe Flanges and Flanged Fittings: Classes 25, 125, and 250; 2020.

      - ASME B16.5 - Pipe Flanges and Flanged Fittings: NPS 1/2 through NPS 24 Metric/Inch Standard; 2020.

      - ASME B31.3 - Process Piping; 2024.

      - ASSE 1001 - Performance Requirements for Atmospheric Type Vacuum Breakers; 2021.

      - ASSE 1012 - Performance Requirements for Backflow Preventers with an Intermediate Atmospheric Vent; 2021.

      - ASSE 1013 - Performance Requirements for Reduced Pressure Principle Backflow Prevention Assemblies; 2021.

      - ASSE 1015 - Performance Requirements for Double Check Backflow Prevention Assemblies; 2021.

      - ASSE 1020 - Performance Requirements for Pressure Vacuum Breaker Assemblies; 2020.

      - ASTM A47/A47M - Standard Specification for Ferritic Malleable Iron Castings; 1999, with Editorial Revision (2022).

      - ASTM C552 - Standard Specification for Cellular Glass Thermal Insulation; 2022.

      - ASTM F1199 - Standard Specification for Cast (All Temperatures and Pressures) and Welded Pipe Line Strainers (150 psig and 150°F Maximum); 2021.

      - ASTM F1200 - Standard Specification for Fabricated (Welded) Pipe Line Strainers (Above 150 psig and 150°F (1 MPa and 65°C)); 2021a.

      - AWWA C508 - Swing-Check Valves for Waterworks Service, 2-In. Through 48-In. (50-mm Through 1,200-mm) NPS; 2017.

      - AWWA C510 - Double Check-Valve Backflow Prevention Assembly; 2017 (Reaffirmed 2021).

      - AWWA C511 - Reduced-Pressure Principle Backflow Prevention Assembly; 2017 (Reaffirmed 2021).

      - AWWA C606 - Grooved and Shouldered Joints; 2022.

    - SUBMITTALS

      - See Section 013000 - Administrative Requirements,  and Section 460500 for submittal procedures.

      - Product Data:  Manufacturer's data sheets for each item of equipment and material provided, showing compliance with requirements; include materials, pressure ratings, seats and seals, clearances for operation and maintenance, and other characteristics.

      - Operating and Maintenance Data:  See Section 460106.

      - Maintenance Materials:

        - For Each Type and Size of Valve:

          - Lubricator, lubricant of appropriate temperature rating, lubricator/isolating valve.

          - Gaskets; 2 each.

          - O-ring seals; 2 each.

          - Diaphragms (molded); 2 each.

          - All other parts made of elastomeric materials; 2 each.

          - Stem packing; 2 each.

          - Seat rings; 2 each and seat ring pulling tool.

        - One set of special tools necessary for adjustment, operation, maintenance and disassembly.

    - QUALITY ASSURANCE

      - Manufacturer Qualifications:  Company specializing in manufacturing the Products specified in this section with not less than one years documented experience.

  - PART 2  PRODUCTS

    - GENERAL REQUIREMENTS

      - Valve and Equipment Inlet, Outlet, and End Connections:  To suit pipe jointing method specified for pipe in which item is to be installed.

    - BACKFLOW PREVENTERS

      - Manufacturers:

        - Zurn Industries, Inc:  www.zurn.com/#sle.

    - PRESSURE REDUCING VALVES

      - Manufacturers:

        - Zurn Industries, LLC; ZW209:  www.zurn.com/#sle.

      - Size 1/2 inch (15 mm, DN) and Larger:

        - Inlet:  Up to ____ gpm (____ Lpm) at inlet pressure of  ____ psi (____ kPa).

        - Outlet:  Pressure set at ____ psi (____ kPa).

        - Function:  Normally open to maintain constant downstream pressure regardless of fluctuations in flow or upstream pressure and prevent backflow; externally mounted strainers with cocks.

        - Operation:  Direct operated, diaphragm actuated, pilot controlled

        - Body:  Angle design; cast iron.

        - Trim and Stem:  Stainless steel.

    - VENTING DEVICES

      - Manufacturers:

        - Zurn Industries, Inc:  www.zurn.com/#sle.

  - PART 3  EXECUTION

    - EXAMINATION

      - _________________________________.

    - PREPARATION

      - _________________________________.

    - INSTALLATION

      - Install in accordance with manufacturer's instructions.

      - Automatic Valve Systems:  Provide the services of equipment manufacturer's technician to supervise installation, adjustment, start-up, demonstration, and testing.

      - Backflow Preventers:  Install in accordance with applicable codes.

        - Install with nameplate and test cocks accessible from front of unit, with a minimum clearance between port and grade of 12 inches (305 mm).  Avoid vertical installation.

      - Sample Ports:  Locate where easily accessible; avoid potential stagnant points and other areas where sample taken might not be typical.

      - Insulation:  Install insulation and jacketing weather tight and in accordance with manufacturer's instructions.

      - Heat Tracing Tape:  Install in accordance with manufacturer's instructions.

    - FIELD QUALITY CONTROL - PRIOR TO STARTUP

      - Demonstrate proper operation of each equipment item.

      - Valves:  Demonstration may occur while testing pipelines or as a separate step.

        - Exception:  Demonstrate operation of air and vacuum relief valves as the pipe is being filled to verify venting and seating.

        - Show that valves open and close smoothly with operating pressure on one side and atmospheric pressure on the other, and in both directions for two-way valve applications.

        - Count and record the number of turns required to open and close each valve, and account for any discrepancies with manufacturer's data.

      - Relief and Regulating Valves:  Set, verify, and record pressure settings.

      - Self-Actuating Valves:  Demonstrate at both maximum and minimum operating ranges and reset upon completion to design value.

    - Owner PERSONNEL TRAINING

      - See Section 460500 for additional requirements.

      - Content:  For identical equipment in multiple locations, identify all locations and any variations in function.

      - Operating Personnel Training:

        - Sessions:  One.

        - Trainees:  Two.

        - Training Hours:  1, minimum, per unique equipment item.

      - Maintenance Personnel Training:

        - Sessions:  One.

        - Trainees:  Two.

        - Training Hours:  1, minimum, per unique equipment item.

    - FIELD QUALITY CONTROL - AFTER STARTUP

      - _________________________________.

- END OF SECTION